## #1
GS EP INS 137 - Appendix 2 - Valve/Actuator Functional Tests
CLIENT: |  | ………. |  |  |  |  | Project Reference: |  |  |  | ……….
Valve Tag Number: |  |  | ………. |  |  |  | Valve S/N: |  | ………. | [5 empty] | Actuator S/N: |  |  | ……….
Reference Documents | [6 empty] | Number | [7 empty] | Revision |  |  | Date
Purchase Order
Valve Data Sheet
General Assembly Drawing
Control Schematic Diagram
Torque Table
1. Conformity Checking
Checks to be performed | [11 empty] | Check results | [5 empty] | Comments
● Valve Type / Bore / Diameter | [6 empty] | ………. | ………. |  | ……….
● Valve Rating / End Connections | [6 empty] | ………. |  | ……….
● Actuator Type: | [6 empty] | ……….
● Control Cabinet Type: | [6 empty] | ……….
● Actuator End Stops checking (alignment between valve & actuator) | [6 empty] | OPEN |  |  |  |  | CLOSE
● Labeling (to be in accordance with General & Project Specifications)
- Trafollyte label on control cabinet front door
- Trafollyte labels at cabinet inlets & outlets connections
- Trafollyte labels on components
- Trafollyte label on limit switches box
- Trafollyte instruction plates
- Stainless Steel name plate on instruments
- Stainless Steel name plate on valve
- Stainless Steel name plate on actuator
- Stainless Steel name plate on reserve vessel
● Control Cabinet: components type & reference
● Control Cabinet & Components: material
● Control Cabinet: components & connections diameters
● Control Cabinet: breathing/venting
● Control Cabinet: draining
● ATEX / IECEx Certification: electrical components
● ATEX / IECEx Certification: cable glands
● ATEX / IECEx Certification: valve + actuator assembly
● Grounding of instruments inside the cabinet
● Control Cabinet earthing facility
● Limit switches type | [6 empty] | ……….
● Valve position beacon indicator
● Valve position mechanical indicator
● Dimensional checking: actuator
● Dimensional checking: cabinet
● Visual checking: reserve vessel
● Painting |  |  |  | Type |  |  |  | Color |  |  |  |  | Thickness |  |  |  |  | Aspect
- Actuator
- Safety accumulator
- Control cabinet
2. Other Verifications to be performed before functional tests
● Actuator power supply
● Operating pressure or voltage | [6 empty] | ………. |  | barg |  | ………. |  |  | volt
● Pilot supply
● Pilot pressure or voltage | [6 empty] | ………. |  | barg |  | ………. |  |  | volt
● Instrument tubes between control panel and actuator are as per future site conditions | [9 empty] | - diameter
- thickness
- length
3. Functional Tests
3.1 Open / Close Commands test (local and remote)
Test operations | [5 empty] | Test results | [6 empty] | Check results |  |  |  |  | Comments
1. Solenoid #1 is not energized & Solenoid #2 is not energized | [5 empty] | â valve is in the safety position
● check beacon indication
● check limit switches contacts
2. Put the local control in the "Remote" position | [5 empty] | â valve stays in position
● check beacon indication
● check limit switches contacts
3. Energize solenoid valve #1 | [5 empty] | â valve stays in position
● check beacon indication
● check limit switches contacts
4. Energize solenoid valve #2 | [5 empty] | â valve moves to normal position
● check beacon indication
● check limit switches contacts
5. Put the local control in the "Close" position (Note: "Open" position for BDVs) | [5 empty] | â valve moves to safety position
● check beacon indication
● check limit switches contacts
6. Put the local control in the "Remote" position | [5 empty] | â valve moves to normal position
● check beacon indication
● check limit switches contacts
7. De-energize solenoid valve #1 | [5 empty] | â valve moves to safety position
● check beacon indication
● check limit switches contacts
8. Energize solenoid valve #1 | [5 empty] | â valve moves to normal position
● check beacon indication
● check limit switches contacts
9. De-energize solenoid valve #2 | [5 empty] | â valve moves to safety position
● check beacon indication
● check limit switches contacts
3.2 Partial Stroking test
Test operations | [5 empty] | Test results | [6 empty] | Check results |  |  |  |  | Comments
1. Check solenoid valve is energized | [5 empty] | â valve is open
2. Turn and release the "Valve Stroke Test" key | [5 empty] | â valve moves 15% to its safety position and returns to normal operating position
3. Functional Tests (Cont'd)
3.3 Solenoid Valve test
Test operations | [5 empty] | Test results | [6 empty] | Check results |  |  |  |  | Comments
1. Energize the solenoid valve(s) | [5 empty] | â pressure at "Solenoid Outlet" gauge is at supply pressure
2. Turn the "Signal Test" key in the "Override" position | [5 empty] | â the pressure switch signal moves to "Test ON"
3. De-energize solenoid #1 | [5 empty] | â pressure at "Solenoid Outlet" gauge is zero
4. Energize solenoid valve #1 | [5 empty] | â pressure at "Solenoid Outlet" gauge is at supply pressure
5. De-energize solenoid #2 | [5 empty] | â pressure at "Solenoid Outlet" gauge is zero
6. Energize solenoid valve #2 | [5 empty] | â pressure at "Solenoid Outlet" gauge is at supply pressure
7. Release the key back to "Service" position | [5 empty] | â the pressure switch signal moves to "Test OFF"
THE VALVE STAYS IN POSITION ALL ALONG THE TEST
3.4 Operating Time
Parameters | [6 empty] | Required Values |  |  | Results |  |  |  | Check Results |  |  |  | Comments
Valve Diff. Pressure | [6 empty] | ………. | bar |  | ………. |  | bar
Min. Actuator Oil / Air supply pressure | [6 empty] | ………. | barg |  | ………. |  | barg
● Closing Time | [6 empty] | ………. | sec |  | ………. |  | sec
● Opening Time | [6 empty] | ………. | sec |  | ………. |  | sec
Max. Actuator Oil / Air supply pressure | [6 empty] | ………. | barg |  | ………. |  | barg
● Closing Time | [6 empty] | ………. | sec |  | ………. |  | sec
● Opening Time | [6 empty] | ………. | sec |  | ………. |  | sec
4.5 BDV Timer test
Parameters | [6 empty] | Required Values |  |  | Results |  |  |  | Check Results |  |  |  | Comments
Accumulator Volume | [6 empty] | ………. | litre |  | ………. |  | litre
Accumulator precharged value | [6 empty] | ………. | barg |  | ………. |  | barg
Time Delay adjustment range | [6 empty] | min | ………. |  | sec |  | max |  | ………. |  | sec
Set Time Delay before BDV Opening | [6 empty] | ………. | sec |  | ………. |  | sec
4.6 Reserve Vessel (Double Acting Actuators)
Parameters | [6 empty] | Required Values |  |  | Results |  |  |  | Check Results |  |  |  | Comments
Accumulator Volume | [6 empty] | ………. | litre |  | ………. |  | litre
Number of strokes - starting from…
… minimal pressure |  |  | ………. |  | barg |  | ………. | strokes |  | ………. |  | strokes
… nominal pressure |  |  | ………. |  | barg |  | ………. | strokes |  | ………. |  | strokes
4.7 Additional Tests for Electrical Actuators
Opening stops on |  |  | Limit Switch | [6 empty] | Closing stops on |  |  |  |  | Limit Switch
|  |  | Torque Limitor | [11 empty] | Torque Limitor
NOTE:
Specific functional tests might be required for devices like Smart Valve Test System (SVTS), Electrical Actuator local control station, etc, with connection to external interfacing or acquisition systems. The test procedure shall be prepared by the supplyer of these devices, and attached to this check-list.
TESTS RESULTS / PROVISORY ACCEPTANCE
EQUIPMENT IS |  |  | ACCEPTED | [5 empty] | WITH |  |  |  |  | WITHOUT |  |  |  |  | PUNCH LIST
EQUIPMENT MUST BE RESUBMITTED BEFORE SHIPMENT
COMMENTS:
| MANUFACTURER |  |  |  |  | INSPECTION Rep. |  |  |  |  | THIRD PART INSP. | [5 empty] | COMPANY Rep.
Date:
Name:
Visa: